# Standard Operating Procedure: Periodic Inspections and Annual Maintenance of Fire Extinguishers

# Purpose

This SOP provides detailed steps to ensure fire extinguishers are properly inspected and maintained according to safety standards. Following these procedures ensures your fire extinguisher remains in proper working condition and complies with safety regulations.

# Scope

This procedure applies to the periodic inspection, annual maintenance, six-year teardown, and safe discharge/chemical recovery of fire extinguishers. Always refer to the manufacturer's manual for specific recharge and maintenance procedures.

# Required Equipment

Fire extinguisher to be inspected

Manufacturer's recharging procedure manual

Closed recovery system for chemical removal (for teardown/discharge steps)

# Part 1: Periodic Inspection Steps

## Step 1: Place the extinguisher in a designated area

Ensure the extinguisher is located in its assigned spot and is not blocked by any objects. The extinguisher should be easily accessible at all times.

A fire extinguisher placed on a table, with a person standing behind it in a demonstration setting. The extinguisher is clearly visible and unobstructed.

## Step 2: Check the tamper seal

Inspect the tamper seal to confirm it is intact and has not been broken.

## Step 3: Verify the pressure gauge

Examine the gauge to ensure it reads within the correct pressure range as indicated on the dial.

A person pointing to the pressure gauge on the fire extinguisher, demonstrating how to check the gauge reading.

## Step 4: Ensure the label is legible

Confirm that the instruction label on the extinguisher is present, correct, and easy to read.

## Step 5: Weigh or heft the cylinder

Lift or weigh the extinguisher to verify it has not lost pressure or contents. Compare the weight to the value listed on the label.

Close-up of hands holding the fire extinguisher, showing the instruction label and demonstrating how to heft or weigh the cylinder.

## Step 6: Inspect for damage or corrosion

Check the cylinder body for any visible signs of damage, dents, or corrosion.

# Part 2: Annual Maintenance Steps

## Step 1: Check the label for legibility

Make sure the label is still readable and contains all required information.

## Step 2: Locate the weight and manufacture date

On the back of the label, find the listed weight of the cylinder and the manufacture date.

Person standing behind the fire extinguisher, referencing the label for weight and manufacture date.

## Step 3: Hydrostatic testing

Safety note: Every 12 years, ensure the cylinder undergoes hydrostatic testing as required.

## Step 4: Test freedom of movement on parts

Squeeze the levers and handles to confirm they move freely. Check that the safety pin is not stuck and can move as intended.

Close-up of hands squeezing the extinguisher's handle and lever to check for freedom of movement.

## Step 5: Verify the tamper seal again

Confirm the tamper seal is still unbroken.

Close-up of hands inspecting the tamper seal and safety pin on the extinguisher.

## Step 6: Remove the hose and inspect for corrosion

Detach the hose from the valve body. Check for corrosion at the connection point. Look for any dry chemical residue in the valve body, which may indicate previous discharge.

Hands removing the hose from the fire extinguisher and inspecting the connection for corrosion.

## Step 7: Check for residual dry chemical

Safety note: If any dry chemical is found in the valve body, the extinguisher must be fully disassembled, cleaned, and recharged according to the recharging procedure.

Hands pointing to the valve body of the extinguisher, with on-screen text explaining the need for teardown if dry chemical is present.

## Step 8: Inspect the gauge for damage

Ensure the gauge is not bent or damaged. If the gauge is damaged, replace the entire cylinder. If the pressure is low and no leaks are found, follow the recharge procedure as outlined in the manual.

# Part 3: Six-Year Teardown

## Step 1: Perform a complete teardown every six years

At six years, disassemble the extinguisher completely and evaluate all parts for integrity. Conduct an internal inspection as required. Refer to the manufacturer's recharging procedure for detailed instructions on teardown, cleaning, and repressurization.

Text slide explaining the six-year teardown requirement and referencing the recharging procedure video for detailed instructions.

# Part 4: Safe Discharge and Chemical Recovery

## Step 1: Ensure the extinguisher is completely empty and depressurized

Safety note: Before performing any maintenance or teardown, confirm that the extinguisher is fully discharged and there is no residual pressure. This is a critical safety step to prevent accidental discharge or injury.

## Step 2: Use a closed recovery system for chemical removal

Several closed recovery systems are commercially available for safely removing and recovering the extinguishing agent. Always use a closed recovery system to prevent the loss of chemical fines (the smallest particles of the extinguishing agent). Loss of these fines can reduce the efficiency of the extinguisher after recharging.

## Step 3: Reference additional resources for detailed procedures

For more information on teardown, cleaning, and recharging, refer to the manufacturer's recharging procedure video. Visit the product section at the manufacturer's website for comprehensive guides and support: AMEREX-FIRE.COM

A person in a red shirt standing behind a fire extinguisher on a table, with the website "AMEREX-FIRE.COM" prominently displayed at the bottom. The setting is a neutral demonstration environment.

## Step 4: Verify all steps are complete before returning the extinguisher to service

Double-check that the extinguisher is reassembled, recharged, and passes all inspection points before placing it back in its designated location.

# Additional Information and Support

All training information, detailed procedures, and product support can be found at the manufacturer's website under the product section.

Look for the diamond logo as a mark of quality and authenticity.

The AMEREX logo, featuring a diamond shape with a red flame above the company name, on a white background.

# Verification and Summary

Confirm the following before considering the process complete:

All periodic inspection points have passed (location, tamper seal, pressure gauge, label, weight, and physical condition).

Annual maintenance checks have been completed, including hydrostatic testing where applicable (every 12 years), freedom of movement of parts, tamper seal integrity, hose and valve inspection, and gauge condition.

Six-year teardown has been performed if due, following the manufacturer's recharging procedure.

The extinguisher has been fully discharged and depressurized before any maintenance or teardown, using a closed recovery system to prevent loss of chemical fines.

The extinguisher is fully reassembled, recharged, and passes all inspection points before being returned to service.

By following these steps and utilizing the recommended resources, you ensure your fire extinguisher is safely maintained, recharged, and ready for use in compliance with industry standards. Always prioritize safety and refer to manufacturer documentation for specific instructions.